Advantages of Using Molten Salt

A variety of fluids was tested to transport the sun's heat, including water, air, oil, and sodium, before molten salt

was selected as best. Molten salt is used in solar power tower systems because it is liquid a atmosphere pressure, it

provides an efficient, low-cost medium in which to store thermal energy, its operating temperatures are compatible with

todays high-pressure and high-temperature steam turbines, and it is non-flammable and nontoxic. In addition, molten

salt is used in the chemical and metals industries as a heat-transport fluid, so experience with molten-salt systems exists

for non-solar applications.

The molten salt is a mixture of 60 percent sodium nitrate and 40 percent potassium-nitrate, commonly called

saltpeter. The salt melts at 430 F and is kept liquid at 550 F in an insulated cold storage tank. The salt is them pumped

to the top of the tower, where concentrated sunlight heats it in a receiver to 1050 F. The receiver is a series of

thin-walled stainless steel tubes. The heated salt then flow back down to a second insulated hot storage tank. The size

of this tank depends on the requirements of the utility; tanks can be designed with enough capacity to power a turbine

from two to twelve hours. When electricity is needed from the plant, the hot salt is pumped to a conventional

steam-generating system to produce superheated steam for a turbine/generator.

The uniqueness of this solar system is in de-coupling the collection of solar energy from producing power,

electricity can be generated in periods of inclement weather or even at night using the stored thermal energy in the hot

salt tank. The tanks are well insulated and can store energy for up to a week. As an example of their size, tanks that

provide enough thermal storage to power a 100-megawatt turbine for four hours would be about 30 feet tall and 80

feet in diameter. Studies show that the two-tank storage system could have an annual efficiency of about 99 percent.

Contact A. R. Mahoney

Sandia National Laboratories, Mail Stop 1127

Albuquerque, NM 87185

Phone: 505-845-3295

FAX: 505-845-3366